## Disclaimer
LOS ANGELES COMMUNITY COLLEGE DISTRICT DEPARTMENT OF FACILITIES PLANNING AND DEVELOPMENT SUSTAINABLE BUILDING PROJECT
PROJECT DESIGN COORDINATION CHECKLIST
DISCLAIMER
The Project Design Coordination Checklist posted on the BuildLACCD website under Project Related Resources; Templates, Forms & Checklists; Section 02 DES Design Procedures is provided strictly as a tool for your use. It is in no way meant to be construed as an all-encompassing checklist nor as a replacement for other checklists that are required by either DSA or the PMO.

## Checklist TOC
PROJECT DESIGN COORDINATION CHECKLIST
TABLE OF CONTENTS
Tab | Checklist | Number of Items
1 | Disclaimer
3 | Cover Sheet
4 | Architecture 590 Checklist | 15
5 | Architecture 600 Checklist | 90
6 | Structural 600 Checklist | 67
7 | Mechanical 600 Checklist | 47
8 | Plumbing 600 Checklist | 32
9 | Electrcal l 600 Checklist | 60
10 | Elevator 600 Checklist | 15
11 | Kitchen 600 Checklist | 10
12 | Civil 600 Checklist | 29
13 | Landscaping 600 Checklist | 16
14 | Specifications 600 Checklist | 10

## Cover Sheet
PROJECT DESIGN COORDINATION CHECKLIST
Cover Sheet
Campus:
Project Name:
Project ID:
Sub-project ID :
Company:
Reviewer Name :
Signature :
Tab | Section | Date Reviewed
4 | Architecture 590 Checklist
5 | Architecture 600 Checklist
6 | Structural 600 Checklist
7 | Mechanical 600 Checklist
8 | Plumbing 600 Checklist
9 | Electrcal l 600 Checklist
10 | Elevator 600 Checklist
11 | Kitchen 600 Checklist
12 | Civil 600 Checklist
13 | Landscaping 600 Checklist
14 | Specifications 600 Checklist

## 590_Arch
| 590 PHASE CHECKLIST | COORDINATED |  |  | REMARKS
ITEM # | ARCHITECTURAL | YES | NO | N/A
1 | Check paths of exiting to verify fire-rated construction provided at these exit paths
2 | Doors for exiting swing in the direction of travel
3 | Required rated rooms and exits are noted on the small scale plans
4 | ADA fixtures shown where required
5 | ADA access provided in toilet rooms
6 | Roof crickets shown where required
7 | Large scale floor plans match small scale floor plans
8 | Large scale floor plans are consistent with each other
9 | Extent of ceramic wall tile clearly shown in plan and elevation
10 | Ceiling heights on reflected ceiling plan matches finish schedule
11 | Location of walls on reflected ceiling plan match floor plans
12 | Full height walls clearly shown on reflected ceiling plan
13 | Bottom of shafts shown and detailed
14 | Room finish schedule matches plans and elevations, including room names, room numbers, finishes, ceiling material and ceiling height
15 | Door schedule matches plans and elevations including sizes, types and labels
16 | All exterior walls, roofs and the underside of exposed suspended slabs shall have insulation
17 | Interior elevations consistent with floor plans
18 | Stair risers do not exceed 7"
| College: | Project Name:
| Reviewer: | Signature:
| Company: | Date:

## 600_Arch
| 600 PHASE CHECKLIST | COORDINATED |  |  | REMARKS
ITEM # | ARCHITECTURAL | YES | NO | N/A
1 | Property lines on survey or civil match architectural
2 | Sheet titles match index
3 | All sheets oriented in the same direction
4 | All floor plan sheets to have north arrow
5 | Building Is located behind set-back lines
6 | Overall building dimensions match structural
7 | Column grid lines match structural
8 | Column and shear wall locations match structural
9 | Column orientation match structural
1O. | Existing and new work clearly defined on site plans
11 | All interior walls located
12 | All doors located by dimension or by typical detail
13 | Stair shafts are dimensioned and dimensions match structural
14 | Elevator shafts are dimensioned and dimensions match structural
15 | Mechanical plumbing shafts are dimensioned and dimensions are consistent with structural and mechanical plumbing
16 | Slab depressions shown match structural
17 | Sloping floors for drainage match structural and plumbing
18 | Electrical panel boards located In rated walls with detail
19 | Location of fire hose cabinets match plumbing
20 | Provide exit signs at each exit door and at each exit corridor change of direction
21 | Exit sign locations match electrical
22 | Doors at electrical vaults and main electrical rooms swing out of these rooms and are provided with panic bars
23 | Provide two exits at main electrica1rooms when electrical service exceeds 1,200 amps
24 | Architectural exterior door locations match civil and landscaping
25 | Architectural exterior door threshold elevations match civil elevations
26 | Elastomeric coating and floor drains provided at supply air plenums
27 | Verify handicap path of travel
28 | Plumbing fixture number and location to match plumbing
29 | Floor sink and floor drain locations match plumbing
30 | Check structural diagonal bracing for penetration of architectural and mechanical items
31 | Check structural diagonal bracing for penetration of space behind exterior
32 | Elevator guide rail tubes and counterweight tubes shown on plans
| 600 PHASE CHECKLIST | COORDINATED |  |  | REMARKS
ITEM # | ARCHITECTURAL | YES | NO | N/A
33 | Architectural equipment requiring power matches electrical
34 | Utility service entrances (gas, water, fire, storm drain, sewer, telephone and electrical) do not interfere with architectural
35 | Roof deck elevations match structural
36 | Fresh air intake shafts and plenums sheet metal lined
37 | Construction of roof slopes match structural and specifications
38 | Roof drain locations match plumbing
39 | Roof drain discharges match civil
40 | Roof slopes 1/4" at valley lines
41 | Roof scuppers shown on elevations
42 | Overflow drain through walls match plumbing
43 | Roof curbs detailed on either architectural or structural
44 | Check for obstructions above top of helipad slab elevation
45 | All roof safety tie-backs and davit sockets located
46 | Structural beams provided at each safety tie-back and davit socket
47 | Floor slabs sloping to floor drains
48 | Dimension strings tied to column grid lines
49 | Dimension strings add to correct amount at large scale plans
50 | A clear dimension of 18" provided at pull side of each interior door
51 | A clear dimension of 24" provided at pull site of each exterior door
52 | Light fixture locations and diffuser locations match electrical and mechanical
53 | Accessible ceiling or ceiling access doors provided at fire damper locations
54 | Elevator machine room duct and pipe enclosures shown
55 | Electrical room duct and pipe enclosures shown
56 | Stair pressurization ducts, hoistway vent ducts and smoke evacuation ducts to be enclosed in a 2-hour enclosure
57 | Duct enclosures match mechanical
58 | Provide section at fire rated corridors
59 | Door hold open devices scheduled on door schedule match electrical locations
60 | High tower locks scheduled on door schedule match electrical locations
61 | Glass lights in doors should be 48" from the floor to the bottom of the light
62 | Door louver locations match mechanical
63 | Building elevations match plans: check roof lines, door and window openings, exterior light fixture and expansion joints
64 | Wall sections match structural
| 600 PHASE CHECKLIST | COORDINATED |  |  | REMARKS
ITEM # | ARCHITECTURAL | YES | NO | N/A
65 | Waterproofing and protection board shown at all below grade walls
66 | Wall sections provided at each exterior wall condition
67 | Finish floor elevations (including stair landings) match structural
68 | Exterior edge of slab matches structural
69 | Size of openings for windows and doors match structural
70 | Exterior louver locations match mechanical
71 | Exterior elevations show pipes, light fixtures, louvers, electrical cabinets
72 | Visible mechanical equipment shown on exterior elevations
73 | Above grade meters shown on exterior elevations and match plumbing locations
74 | Fire Department connection shown on exterior elevations and match plumbing locations
75 | Code required slgnage shown on exterior elevations
76 | Verify glass types with specifications
77 | Location of tempered lights or tempered "knock-out" lights shown in elevation
78 | Exposed concrete walls have finish noted on elevations or specifications
79 | General notes and details for waterproofing coordinated with soils report
80 | Sloping kitchen hood ducts shown on architectural
81 | Seismic joints are continuous throughout building
82 | Verify ceiling heights with room finish schedule
83 | Interior elevations of all major spaces should show visible engineering items
84 | Partial height walls to have miscellaneous steel tubes in wall anchored to slab
85 | Reinforcing for curbs, pads and floating slabs shown on architectural
86 | Counter tops and cabinets deep enough for specified sinks
87 | Architectural elevator shaft sections match structural and elevator consultant drawings
88 | Architectural stair sections match structural
89 | There is a minimum clearance of 7' - 0" at the stair landing
90 | There Is a minimum clearance of 6' - 8" at the stair risers
| College: | Project Name:
| Reviewer: | Signature:
| Company: | Date:

## 600_Struct
| 600 PHASE CHECKLIST | COORDINATED |  |  | REMARKS
ITEM # | STRUCTURAL | YES | NO | N/A
1 | General notes agree with specifications
2 | Column grids match architectural
3 | Column locations match architectural
4 | All columns located wth rectangular grid locations (no radius locations)
5 | Floor elevations match architeclural and civll
6 | Floor datum elevations match architectural
7 | Elevator machine room slab elevations match architectural
8 | Elevator pit elevations match architectural
9 | Check pit elevations .and top of footings
1O. | Provide 7' - 6" clear In elevator machine rooms
11 | Depressed slab locations match architectural
12 | Depressed slabs are detailed
13 | Raised slab locations match archltectural
14 | Raised slab locations are detailed
15 | Roof elevations to match architectural
16 | Roof slopes match architectural
17 | All footing sizes are noted and footing elevations provided
18 | ooting/foundation material complies with geotechnical report
19 | Stepped footings shown on foundation plan
20 | Foundation beams are identified and listed in a schedule
21 | Check location and depth of underground piping versus location and depth of footings
22 | Check sump pit locations and depths versus location and depth of footings
23 | Check location and depth of utilities penetrating exterior walls versus framlng and footings
24 | Under slab subgrade preparation shown on plan and details
25 | Under slab subgrade preparation complies with geotechnical report
26 | Structural work complies with geotechnical report
27 | Section through building to show over-excavation below slab and footings if over-excavation is required
28 | Check footings/foundations for offset conditions not detailed
29 | Footing elevations agree with site grades shown on civil
30 | Edge of slab locations match architectural
31 | Edge of slab-on grade detail matches architectural
32 | Construction joint and control joint layout shown on the slab-on-grade
33 | All columns listed in column schedule
34 | Column schedule lists correct length ot each column
| 600 PHASE CHECKLIST | COORDINATED |  |  | REMARKS
ITEM # | STRUCTURAL | YES | NO | N/A
35 | Verify column sizes on frame elevations
36 | Concrete column encasements match architectural
37 | Structural steel reinforced concrete Interfaces to be checked for rebar clearance
38 . | All beams listed on the beam schedule
39 | Each steel beam has size shown
40 | Each concrete beam has a scheduled beam type
41 | All beams are located in plan
42 | Top of beams framing into each other shall match
43 | Bottom of floor framing beams shall be above bottom of girders
44 | Beam sleeves shown in concrete beams
45 | Beam pipe penetrations shown in steel beams
46 | Beam duct penetrations shown in steel beams
47 | Shear studs noted on beams where required
48 | Indicate camber where required in floor and roof beams
49 | Slab openings dimensioned
50 | Slab openings match architectural
51 | Slab openings for electrical bus risers shown
52 | There is a minimum clearance of 7-0" at stair landings
53 | Expansion joint locations match architectural
54 | In concrete slabs, all slab openings should have reinforcing shown
55 | Required elevator guide rails supports shown
56 | Required elevator counterweight rail supports shown
57 | Show door and duct openings in concrete shear walls
58 | Concrete reinforcing clearly shown at arched openings
59 | Roof openings match architectural and mechanical
60 | Roof framing at stairs provided to hang stair landing hanger rods
61 | Bracing of bottom beams flanges at precast panels shown
62 | Roof tie down locations match architectural (lateral bracing at bottom beam flanges may be required)
63 | Davit socket locations match architectural
64 | MechanicaVhousekeeping pads shown on structural or architectural
65 | Rebar splice lengths are defined in feet and Inches
66 | Special structural details (x-bracing, beam bracing, outriggers) do not conflict with architectural, plumbing or mechanical)
67 | Site retaining walls shown on structural,civil or landscaping
| College | Project Name:
| Reviewer: | Signature:
| Company:: | Date:

## 600_Mech
| 600 PHASE CHECKLIST | COORDINATED |  |  | REMARKS
ITEM # | MECHANICAL | YES | NO | N/A
1 | Mechanical room plans match architectural plans
2 | Mechanical roof plan matches architectural roof plan
3 | Mechanical roof openings match structural roof openings
4 | Mechanical equipment locations match structural
5 | Building skin and glazing materials match Title 24 calculations (including IDM, BIM/REVIT)
6 | All equipment shown on schedules
7 | All equipment shown on schedules also shown on plans
8 | Control air compressors scheduled with wiring and control diagrams
9 | Ceiling diffusers and grilles match architectural reflected ceiling plan (including BIM/REVIT)
10 | Check beam'duct clearances above ceiling
11 | Check beam clearances above ceiling at underside of roof taking into account sloping roof structure
12 | Trace major ducts to determine interference with architectural, structural and plumbing (including BIM/REVIT)
13 | At distribution loops the bottom of the duct insulation should be 6" above the proposed ceiling line
14 | Ducts in shafts are sized to fit into the architectural shafts
15 | Supply air intake openings shown on architectural
16 | Exhaust air openings shown on architectural
17 | Ventilation CFM's for smoke evacuation are shown on the drawings
18 | Dampers located in all fire walls and rated ceilings
19 | Combustion air provided for fuel burning equipment (generators, furnaces, boilers, water heaters)
20 . | Mechanical equipment power requirements match electrical
21 | Ducts and piping should not run through electrical rooms orelevator machine rooms (including BIM/REVIT)
22 . | Location of halon dampers matches electrical
23 | Elevator hoistway venting to match architectural
24 | Make-up air provided for boilers and water heaters
25 | Emergency generator room adequately ventilated
26 | Elevator hoistway vent to be sheet metal lined
27 . | AJC for elevator machine rooms to be located outside of the machine rooms
28 | Mechanical housekeeping pads shown and detailed on architectural or structural
29 | Extent of sound attentuation to be reasonable for the occupancy
30 | Each room has supply and retum/exhaust air (including BIM/REVIT)
31 | Verify VAV zones based upon occupancy of spaces (including BIM/REVIT)
| 600 PHASE CHECKLIST | COORDINATED |  |  | REMARKS
ITEM # | MECHANICAL | YES | NO | N/A
32 | Return air wall openings provided at an full height walls
33 | Thermostats are not located on glass walls or windows
34 | Architectural door louvers provided where shown on mechanical
35 | The CFM required from each VAV box does not exceed the VAV box capacity
36 | The mechanical plans match the control drawing systems schematic
37 | Kitchen equipment connections match kitchen drawings
38 | Sloping hood exhaust ducts shown
39 | Provide make-up air for kitchen exhaust hoods
40 | Fire/life safety sequence Included in drawing set
41 | EMCU and EMS panels located in plan
42 | Duct lining is clearly shown
43 | Heat gain In elevator machine rooms has been defined by the elevator consultant
44 | All heat producing equipment Is located and identified
45 | Supply and return piping provided at remote condensers
46 | Drain line provided from fan coil units and packaged A/C units
47 | Outside air plenums are sheet metal lined
| College: | Project Name:
| Reviewer: | Signature:
| Company: | Date:

## 600_Plumbing
| 600 PHASE CHECKLIST | COORDINATED |  |  | REMARKS
ITEM # | PLUMBING | YES | NO | N/A
1 | Plumbing fixture locations match architectural (including BIM/REVIT)
2 | Location and type of fire department connection matches architectural
3 | Roof drain locations match architectural
4 . | Plumbing utility plan locations and elevations match civil
5 . | Trace large plumbing lines to determine interferences with architectural, structural and mechanical (including BIM/REVIT)
6 | Required beam penetrations are located in plan and elevation on structural
7 | Verify plumbing riser locations In relation to floor beams
8 | Locate underground piping in plan and elevation In relation to the footings
9 | Foundation/under slab drainage matches civil and geotechnical report
10 | Locate floor drains, floor sinks and sump pits In relation to footings
11 | Location of site sump pumps matches civil
12 | Piping should avoid electrical rooms and elevator machine rooms
13 | Sufficient clear spaces provided at plumbing chases for pipes and carriers
14 | Plumbing electrical requirements match electrical
15 | Architectural plumbing chases are provided for plumbing risers
16 | Fire hose cabinet locations match architectural
17 | Floor sinks provided for mechanical equipment
18 | Provide make-up water line with backflow device for cooling towers
19 | Provide floor sink at each cooling coil bank
20 | Coordinate location of above ground site valves and backflow preventers with civil and landscaping (including BIM/REVIT)
21 . | Heating hot water systems will provide hot water within a reasonable time
22 . | Plumbing flow switch/tamper switch locations match electrical plans andfire/life safety riser
23 . | Exterior horizontal mechanical openings in slabs and roofs have drain and storm drain piping
24 | Emergency generator muffler and exhaust piping is shown
25 | Storage tanks coordinated with structural
26 | Fire protection tank coordinated with structural
27 | Verify underground fuel tanks are double-walled with a leak detection system
28 | Irrigation pcint of connection matches landscape drawings
29 | Provide trap primers for floor drains and floor sinks
30 | Provide plumbing connections as shown on the kitchen drawings
| 600 PHASE CHECKLIST | COORDINATED |  |  | REMARKS
ITEM # | PLUMBING | YES | NO | N/A
31 | Provide fire protection for kitchen hoods
32 | Provide grease trap for kitchen equipment
| College: | Project Name:
| Reviewer: | Signature:
| Company: | Date:

## 600_Elect
| 600 PHASE CHECKLIST | COORDINATED |  |  | REMARKS
ITEM # | ELECTRICAL | YES | NO | N/A
1 | Main electrical room has sufficient space for electrical and transformers (room and equipment drawn to scale)switchgear
2 | Each electrical room has sufficient space for panels and transformers (room and equipment drawn to scale)
3 | Housekeeping pads shown on architectural or structural
4 | Emergency generator room sized for largest generator model
5 | Electrical switchgear, transformers and panels have minimumrequired clearances
6 | Panel boards·not in electrical rooms match architectural locations
7 | Location of equipment on electrical matches mechanical and plumbing
8 | Sufficient spare capacity provided at main switchgear, motor control centers and emergency generators
9 | Check location of vertical bus risers with location of structural beams
10 | Slab openings for bus risers match structural locations
11 | Does architectural have equipment that requires power?
12 | Power for architectural equipment maches architectural
13 | Power for mechanical equipment matches mechanical power requirements
14 | Power for plumbing equipment matches plumbing power requirements
15 | Location of light fixtures match architectural ceiling plan
16 | All wall mounted lights have mounting height shown
17 | All wall mounted lights are above or beyond door swings
18 | Verify emergency lighting provided where required
19 | All pendant (or chain) mounted lights have mounting height shown
20 | Disconnect switches provided for all mechanical, plumbing and elevator equipment
21 | Fire/life safety riser to show connection to fans and other mechanical/plumbing equipment required to be controlled
22 | Fire/life safety riser to show connection to elevator equipment
23 | Fire alarm control panel is connected to emergency power or has a battery pack
24 | Provide life/safety speakers in mechanical, electrical, and fan rooms
25 | Fire control provided at kitchen hood exhaust ducts
26 | Duct smoke detector quantity and location match mechanical
27 | Receptacles not located in glass walls, windows or behind equipment
28 | Floor mounted receptacles to be dimensioned from grid lines or face of walls.
29 | Floor mounted receptacles to match architectural locations
| 600 PHASE CHECKLIST | COORDINATED |  |  | REMARKS
ITEM # | ELECTRICAL | YES | NO | N/A
30 | Variable frequency drives required by mechanical or plumbing being supplied by electrical
31 | Tamper switch provided at site pressure indicating valves
32 | Telephone conduit provided from group controller to telephone room
33 | Additional disconnect switches at elevator machine rooms were required
34 | Conduit provided from elevator shafts to fire control room
35 | Power provjded to each EMS panel
36 | Power to kitchen equipment is provided per the kitchen drawings
37 | Hanging transformer details shown on architectural
38 | Light switches not located in glass walls, windows or behind equipment
39 | Locate in plan site vaults, transformer pads and duct banks
40 | Locations of underground vaults, manholes and duct banks do not
interfere with civil site utilities
41 . | Location of site light fixtures matches civil and landscaping
42 | Light pole footing detail shown on electrical drawings
43 | Provide power for irrigation controllers
44 | All exterior lighting controlled by one time clock or one photo cell
45 | Exterior light fixtures to be located in plan and elevation
46 . | Lights in fountains and pools must have junction boxes above the water level
47 | Provide lighting on emergency power between the buikiing exits and
the property line
48 . | Each light fixture has a type noted
49 | Each fixture type has been coordinated with the ceiling type (gypsum board, T-bar. fine line)
50 | Sufficient lighting provided in elevator machine rooms
51 . | Provide lights in mechanical enclosures and inside air handlers
52 | Provide emergency lighting in each elevator machine room
53 . | Check visibility of each exit sign
54 | Provide a security riser if there is security in the project
55 | Where there is door security hardware has electrical provideda door elevation showing conduit and location of each security item?
56 | Halon system schematic provided
| 600 PHASE CHECKLIST | COORDINATED |  |  | REMARKS
ITEM # | ELECTRICAL | YES | NO | N/A
57 | Verify that mechanical is providing the fans, ducts and dampers required for halon
58 | A telecommunication riser diagram has been provided
59 | Provide emergency telephones in stairwells (high-rise)
60 | Provide fireman's phone jack In stairwells and elevator lobbies (high-rise)
| College: | Project Name:
| Reviewer: | Signature:
| Company: | Date:

## 600_Elevator
| 600 PHASE CHECKLIST | COORDINATED |  |  | REMARKS
ITEM # | ELEVATOR | YES | NO | N/A
1 | Each elevator shaft dimenisoned in relation to column lines
2 | Each elevator pit dimensioned In relation to column lines
3 | Each elevator platform dimensioned and located within the shaft
4 | Sufficient vertical space provided at top of hoistway
5 | Vertical clearances provided in elevator machine rooms
6 | Each floor must be served by an elevator large enough to be a medical alert elevator
7 | Interior cab elevations and cab reflected ceiling plan provided
8 | Adequate elevator hoistway venting is shown
9 | Motorized damper with actuator outside of hoistway provided at hoistway vent exterior opening
10 | Underslung elevators require large anchor footings at machine room
11 | Are any elevators required to be on emergency power and is this emergency power provided?
12 | Telephone home runs provided at each machine room to 24 hour manned system
13 | In elevator machine rooms there are the following criteria:
A | 10 fc lighting
B | Disconnect switches at the door
C | Possible secondary disconnect switches
D | Fan coil unit located outside of the machine room
E | No pipes or ducts running through the machine room
F | One receptacle on each wall
14 | Sufficient A/C capacity for elevator equipment BTUs
15 | Each elevator pit has a light and convenience outlet
| College: | Project Name:
| Reviewer: | Signature:
| Company: | Date:

## 600_Kitchen
| 600 PHASE CHECKLIST | COORDINATED |  |  | REMARKS
ITEM # | KITCHEN | YES | NO | N/A
1 | Kitchen floor plans match architectural (columns and walls)
2 | Structural shows required slab recesses
3 | Architectural provides required base and floor finishes
4 | Architectural provides required/desired ceiling finishes
5 | Verify hood exhaust rated duct enclosures are provided by architectural
6 | Mechanical provides required HVAC connections
7 | Plumbing provides required fixtures and piping connections
8 | Electrical provides required power
9 | Lighting layout works with kitchen equipment layout
10 | Electrical panels located on kitchen drawings
| College: | Project Name:
| Reviewer: | Signature:
| Company: | Date:

## 600_Civil
| 600 PHASE CHECKLIST | COORDINATED |  |  | REMARKS
ITEM # | CIVIL | YES | NO | N/A
1 | New above·ground work is coordinated with hardscape and landscape
2 | Grades agree with architectural and structural
3 | Grades are consistent with adjoining property conditions
4 | Exterior grades slope away from building
5 | Building located in each direction in relation to the property lines
6 | Finish floor elevations match architectural and structural
7 | Verify handicap requirements for parking, covered parking and building access
8 | Off-site work is coordinated with site work
9 | Limits of construction are consistent with other disciplines
10 | New and existing site easements shown
11 | Required demolition is clearly noted
12 | Removal and replacement of unsuitable soil clearly noted
13 | Each paving type and thickness to be scheduled and graphically located on plan
14 | All hardscape items (curbs,.pads, walls, sidewalks, benches) are detailed on architectural ,civil or landscaping
15 | Fence and garden wall location and details match architectural and landscaping
16 | Above ground utilities are shown on landscaping and architectural site plan
17 | Existing poles, valve boxes and manholes do not Interfere with new horizontal surfaces
18 | New poles, valve boxes and manholes do not interfere with new horizontal surf aces
19 | Subgrade work under paving and sidewalks defined
20 | Underground utilities do not interfere with new or existing work
21 | Utility points of connection at the building agree with plumbing (horizontal locations and vertical elevations)
22 | Planter drain locations match landscape and plumbing
23 | Fire Department site access to the building to be verified
24 | Expansion joints clearly shown on site concrete
25 | Exterior slabs slope away from exterior floors
26 | Top of wall elevations match architectural and structural
27 | Top of curb elevations clearly shown
28 | Specifications for site drains, grades and piping coordinated with plumbing
29 | Specifications identify existence of soils report and instructions for availability
| College: | Project Name:
| Reviewer: | Signature:
| Company: | Date:

## 600_Landscape
| 600 PHASE CHECKLIST | COORDINATED |  |  | REMARKS
ITEM # | LANDSCAPING | YES | NO | N/A
1 | Hardscape plans match architectural and civil
2 | Hardscape elevations match architectural and civil
3 | Limits of construction match architectural and civil
4 | All areas within the project limit of construction have landscape and irrigation
5 | Off-site landscape and Irrigation shown on drawings
6 | All hardscape shown and detailed on architectural , civil or landscaping
7 | Irrigation controllers located in inconspicuous location
8 | Irrigation sleeves shown under hardscape
9 | Irrigation point-of-connection matches plumbing
10 | Expansion joints clearly shown on site concrete work
11 | Site lighting matches electrical
12 | Plant sizes and spacing are scheduled
13 | Tree staking/planting details provided
14 | Above ground utilities shown and surrounded with planting
15 | Site planter or tree well drainage coordinated with civil utility plan
16 | Civil work complies with geotechnical report
| College: | Project Name:
| Reviewer: | Signature:
| Company: | Date:

## 600_Specs
| 600 PHASE CHECKLIST | COORDINATED |  |  | REMARKS
ITEM # | SPECIFICATIONS | YES | NO | N/A
1 | All sections listed in the index provided
2 | All sections complete
3 | Division One complete
4 | Related sections listed part of the specifications
5 | Verify that only specific submittals are required for submission
6 | Each section consistent with the drawings
7 | Verify that all major elements of work are specified
8 | Verify that all specialty and miscellaneous items are specified
9 | Architectural finishes listed in the finish schedule should be specified
10 | Bid alternates should be clearly defined
| College | Project Name:
| Reviewer: | Signature:
| Company: | Date: